## Building Heating Steam
Focus on Energy Business Programs Deemed Savings Calculation
Tech Code: | 4.1000
Group: | HVAC
Category: | Steam Trap
Description: | Repair leaking steam trap, building space conditioning system
Developed by: | Andrew Kotila
Submitted by: | Andrew Kotila
Quality group release date: |  | 2009-06-18 | Evaluation revisions
Evaluation approval date:
Evaluator: | Brian Dunn, KEMA
Note to evaluator: These savings values are intended to replace the previously deemed savings value for tech code 4.1000
Assumptions:
Steam traps are used on a system where the steam use is for building space conditioning (space heating).
This measure is not intended for industrial process steam systems.
Steam is produced through the combustion of natural gas.
960.1 | Latent heat content of steam for 5 psig system (Btu per lb)
952.1 | Latent heat content of steam for 10 psig system (Btu per lb)
945.3 | Latent heat content of steam for 15 psig system (Btu per lb)
Steam trap operating hours per year:
| 2309.7 | Thermostatic Steam Trap
| 4972 | Mechanical (F&T) Steam Trap
|  | 226 | Boiler operating days per year: Assume the boiler is operating any day the high temp is below 65 degrees F
Average of estimated days for EauClaire, LaCrosse, GreenBay, Milwaukee, and Madison based on TMY2 data
|  | 10.2199 | Thermostatic steam trap operating hours per day: Using 7699 heating degree days for Wisconsin (based on Deeming Boilers Modulating 1May08), effective full load heating hours are 2310 hours (7699 HDD * 24 hours/day / (65 deg – (-15 deg)). Operating hours per day for thermostatic steam traps can be estimated as 2310 hours / 226 days = 10.2 hours/day
|  | 22 | Mechanical (F&T) steam trap operating hours per day: Building heating boilers normally operate 24 hrs/day. In a rare instance, the boiler is turned off during the night, therefore 24 hour operation is being reduced to 22 hours to remain conservative.
0% | Percentage of heat lost through steam traps that continues to provide heat to the building
Where the condensate lines run through conditioned space, the heat "wasted" by leaking traps can still add heat to the building.
Where condensate lines run in unconditioned spaces (such as steam tunnels, the "wasted" heat is lost. We assume
the deemed savings that most condensate lines are running in steam tunnels and none of the waste heat provides heating for the building.
0.8 | Standard boiler efficiency. According to the Natural Gas Boiler Burner Consortium typical boiler efficiency will be in the 75 - 85% range.
80% is the midpoint of the range. This is at the high end for a typical steam boiler without heat recovery,
however, heat recovery systems are installed on many boiler plants increasing the efficiency fo the base system.
|  | http://www.energysolutionscenter.org/boilerburner/Eff_Improve/Primer/Boiler_Introduction.asp | [5 empty] | (accessed 18 June 2009)
50% | Assumed equivalent orifice size:
Steam Trap Performance Assessment, Advanced technologies for evaluating the performance of steam traps, Federal Technology Alerts
|  | http://www.plantsupport.com/download/Steam%20Trap%20Performance%20Assessment.pdf | [5 empty] | (accessed 18 June 2009)
Leaking Steam Trap Discharge Rate:
Trap Orifice Diameter (inches) | Leaking Steam Trap Discharge Rate (lb/hr) |  |  | Chart Source: |  |  |  |  | Chart Source:
| Steam Pressure, psig |  |  | Steam Trap Loss Estimator |  |  |  |  | http://uesystems.com/tech_support_charts_steam_loss.asp | (accessed 26-Mar-08)
| 5 | 10 | 15
0.21875 | 14.2837 | 17.7355 | 21.1665 |  | Note: these three orifice sizes are most common in building conditioning steam systems,
0.25 | 18.6562 | 23.1647 | 27.646 |  | per Tim Thuemling (steam trap maintenance service provider), July 2009.
0.3125 | 29.1503 | 36.1948 | 43.1968
| 27.8823 | 34.6203 | 41.3178 | 32.258 | lb/hr (thermostatic)
| 17.0821 | 21.2102 | 25.3134 | 19.7628 | lb/hr (F&T)
Thermostatic Steam Trap:
Trap Orifice Diameter (inches) | Market Prevalence | Energy lost per year through leaks (therms/yr)
|  | Steam Pressure, psig |  |  |  | Source of market prevalence of trap orifice sizes and actual operating
|  | 5 | 10 | 15 |  | steam pressure: Interview with Tim Thuemling, July 2009.
prevalence |  | 45% | 45% | 10% | 100%
0.21875 | 5% | 395.933 | 487.5178 | 577.6747
0.25 | 5% | 517.1369 | 636.7579 | 754.5139 |  |  |  | 6.0636
0.3125 | 90% | 808.0264 | 994.9342 | 1178.928
| 100% | 772.8773 | 951.6546 | 1127.6446 | weighted average therms
|  |  | Annual energy lost, weighted by prevalence of pressure: | 888.8038 | therms
Mechanical (F&T) Steam Trap:
Trap Orifice Diameter (inches) | Market Prevalence | Energy lost per year through leaks (therms/yr)
Steam Pressure, psig
|  | 5 | 10 | 15 |  | Source of market prevalence of trap orifice sizes and actual operating
prevalence |  | 45% | 45% | 10% | 100% | steam pressure: Interview with Tim Theumling, July 2009.
0.21875 | 48% | 852.3092 | 1049.4603 | 1243.5375
0.25 | 47% | 1113.2202 | 1370.7236 | 1624.2123
0.3125 | 5% | 1739.4066 | 2141.7556 | 2537.8317
| 100% | 1019.2923 | 1255.0688 | 1487.1694 | weighted average therms
|  |  | Annual energy lost, weighted by prevalence of pressure: | 1172.1794 | therms
Thermostatic steam traps make up about 90% of the population, mechanical (F&T) traps make up 10%
F&T traps are designed to fail closed but can fail open. According to Mr. Thuemling, these traps will fail open 66 % of the time.
For every 100 traps then, we assume 90 are thermostatic and 10 are F&T.
| Assumed population percentages | Fail open rate | Assumed population percentages that fail open | Weight
Thermostatic | 90% | 90% | 81% | 92.47%
F&T | 10% | 66% | 6.6% | 7.534%
Therefore, market weighted energy lost through leaking steam traps in building heating systems: | [5 empty] | 910.154 | therms
This is what we seek to deem:
Tech Code | Annual therm savings per leaking trap repaired | Measure Description
4.1000.390 | 910.154 | Repair leaking steam trap, building space conditioning system
Note on O47: Brian Dunn: Can not determine the basis of the estimates provided by this source. The rates are similar to those found in the estimator based on Grashof's equation, but not exact.
Note on D30: Brian Dunn: These hours have little effect on the total.
Note on G50: Brian Dunn: Confirmed these numbers with Tim Thuemling
Note on H57: Brian Dunn: Confirmed these numbers with Tim Thuemling
Note on H70: Brian Dunn: Confirmed these numbers with Tim Thuemling

## Steam Trap Loss Estimator
Steam System Absolute Pressure | 30 | psia
Steam System Gauge Pressure | 15.304 | psig
Condensate System Absolute Pressure | 30 | psia
Condensate System Gauge Pressure | 15.304 | psig
Operating Hours | 8760 | hours/year
Latent heat of steam | 945.3 | btu/lb
Heat of Saturated liquid at steam pressure | 218.82 | btu/lb
Heat of Saturated liquid at condensate pressure | 218.82 | btu/lb
Makeup water temp | 60 | deg F
Heat of Saturated liquid for makeup water | 28.08 | btu/lb
Percent Condensate Lost | 0%
Percent Trap Open | 50%
Orifice size | Diameter | Area | lb steam/hr | MMBTU/year
1/32 | 0.03125 | 0.00076699 | 0.43197 | 3.5771
1/16 | 0.0625 | 0.003068 | 1.7279 | 14.3082
3/32 | 0.09375 | 0.0069029 | 3.8877 | 32.1935
1/8 | 0.125 | 0.012272 | 6.9115 | 57.2329
5/32 | 0.15625 | 0.019175 | 10.7992 | 89.4264
3/16 | 0.1875 | 0.027612 | 15.5509 | 128.774
7/32 | 0.21875 | 0.037583 | 21.1665 | 175.2758
1/4 | 0.25 | 0.049087 | 27.646 | 228.9316
9/32 | 0.28125 | 0.062126 | 34.9894 | 289.7416
5/16 | 0.3125 | 0.076699 | 43.1968 | 357.7056
11/32 | 0.34375 | 0.092806 | 52.2682 | 432.8238 |  | Trap Orifice Diameter (inches) | Leaking Steam Trap Discharge Rate (lb/hr)
3/8 | 0.375 | 0.11045 | 62.2035 | 515.0961 |  |  | Steam Pressure, psig
13/32 | 0.40625 | 0.12962 | 73.0027 | 604.5225 |  |  | 5 | 10 | 15
7/16 | 0.4375 | 0.15033 | 84.6658 | 701.1031 |  | 0.21875 | 14.2837 | 17.7355 | 21.1665
15/32 | 0.46875 | 0.17257 | 97.1929 | 804.8377 |  | 0.25 | 18.6562 | 23.1647 | 27.646
1/2 | 0.5 | 0.19635 | 110.5839 | 915.7265 |  | 0.3125 | 29.1503 | 36.1948 | 43.1968
lb steam/hr equation source:
Grashof's Equation: | Q=0.7 x 0.0165 x 3600 x A x P^0.97
where: | Q = flow rate of steam in lbs/hour
0.7 is the coefficient of discharge for hole
A is the area of hole (in2)
P is the pressure inside the steam line (psia)
http://memagazine.asme.org/articles/2009/February/Technology_Focus.cfm |  |  |  |  | (accessed 18 June 2009)
This equation was used to produce the following graph:
from
Steam Trap Performance Assessment, Advanced Technologies for evaluating the performance of steam traps, FEMP, DOE/EE-0193
http://www1.eere.energy.gov/femp/pdfs/FTA_SteamTrap.pdf
This graph is often quoted as the source for energy loss due to steam trap leaks. It assumes any steam lost through the trap is lost. There is no condensate, all condensate must be replaced by make-up water at 60 deg F (energy and condensate are both lost). For steam traps returning condensate, the will overstate the energy lost.

## Steam Table
Col. 1 | Col. 2 | Col. 3 | Col. 4 | Col. 5 | Col. 6 | Col. 7 | Col. 8
Gauge | Absolute | Steam | Heat of | Latent | Total Heat | Specific | Specific
Pressure | Pressure | Temp. | Sat. Liquid | Heat | of Steam | Volume of | Volume of
| (psia) | (°F) | (Btu/lb) | (Btu/lb) | (Btu/lb) | Sat. Liquid | Sat. Steam
[6 empty] | (cu ft/lb) | (cu ft/lb)
29.743 | 0.08854 | 32 | 0 | 1075.8 | 1075.8 | 0.096022 | 3306
29.515 | 0.2 | 53.14 | 21.21 | 1063.8 | 1085 | 0.016027 | 1526
27.886 | 1 | 101.74 | 69.7 | 1036.3 | 1106 | 0.016136 | 333.6
19.742 | 5 | 162.24 | 130.13 | 1001 | 1131 | 0.016407 | 73.52
9.562 | 10 | 193.21 | 161.17 | 982.1 | 1143.3 | 0.01659 | 38.42
7.536 | 11 | 197.75 | 165.73 | 979.3 | 1145 | 0.01662 | 35.14
5.49 | 12 | 201.96 | 169.96 | 976.6 | 1146.6 | 0.016647 | 32.4
3.454 | 13 | 205.88 | 173.91 | 974.2 | 1148.1 | 0.016674 | 30.06
1.418 | 14 | 209.56 | 177.61 | 971.9 | 1149.5 | 0.016699 | 28.04
0 | 14.696 | 212 | 180.07 | 970.3 | 1150.4 | 0.016715 | 26.8
1.3 | 16 | 216.32 | 184.42 | 967.6 | 1152 | 0.016746 | 24.75
2.3 | 17 | 219.44 | 187.56 | 965.5 | 1153.1 | 0.016768 | 23.39
5.3 | 20 | 227.96 | 196.16 | 960.1 | 1156.3 | 0.01683 | 20.09
10.3 | 25 | 240.07 | 208.42 | 952.1 | 1160.6 | 0.016922 | 16.3
15.3 | 30 | 250.33 | 218.82 | 945.3 | 1164.1 | 0.017004 | 13.75
20.3 | 35 | 259.28 | 227.91 | 939.2 | 1167.1 | 0.017078 | 11.9
25.3 | 40 | 267.25 | 236.03 | 933.7 | 1169.7 | 0.017146 | 10.5
30.3 | 45 | 274.44 | 243.36 | 928.6 | 1172 | 0.017209 | 9.4
40.3 | 55 | 287.07 | 256.3 | 919.6 | 1175.9 | 0.017325 | 7.79
50.3 | 65 | 297.97 | 267.5 | 911.6 | 1179.1 | 0.017429 | 6.66
60.3 | 75 | 307.6 | 277.43 | 904.5 | 1181.9 | 0.017524 | 5.82
70.3 | 85 | 316.25 | 286.39 | 897.8 | 1184.2 | 0.017613 | 5.17
80.3 | 95 | 324.12 | 294.56 | 891.7 | 1186.2 | 0.017696 | 4.65
90.3 | 105 | 331.36 | 302.1 | 886 | 1188.1 | 0.017775 | 4.23
100 | 114.7 | 337.9 | 308.8 | 880 | 1188.8 | 0.01785 | 3.88
110.3 | 125 | 344.33 | 315.68 | 875.4 | 1191.1 | 0.017922 | 3.59
120.3 | 135 | 350.21 | 321.85 | 870.6 | 1192.4 | 0.017991 | 3.33
125.3 | 140 | 353.02 | 324.82 | 868.2 | 1193 | 0.018024 | 3.22
130.3 | 145 | 355.76 | 327.7 | 865.8 | 1193.5 | 0.018057 | 3.11
140.3 | 155 | 360.5 | 333.24 | 861.3 | 1194.6 | 0.018121 | 2.92
150.3 | 165 | 365.99 | 338.53 | 857.1 | 1195.6 | 0.018183 | 2.75
160.3 | 175 | 370.75 | 343.57 | 852.8 | 1196.5 | 0.018244 | 2.6
180.3 | 195 | 379.67 | 353.1 | 844.9 | 1198 | 0.01836 | 2.34
200.3 | 215 | 387.89 | 361.91 | 837.4 | 1199.3 | 0.01847 | 2.13
225.3 | 240 | 397.37 | 372.12 | 828.5 | 1200.6 | 0.018602 | 1.92
250.3 | 265 | 406.11 | 381.6 | 820.1 | 1201.7 | 0.018728 | 1.74
| 300 | 417.33 | 393.84 | 809 | 1202.8 | 0.018896 | 1.54
| 400 | 444.59 | 424 | 780.5 | 1204.5 | 0.01934 | 1.16
| 450 | 456.28 | 437.2 | 767.4 | 1204.6 | 0.019547 | 1.03
| 500 | 467.01 | 449.4 | 755 | 1204.4 | 0.019748 | 0.93
| 600 | 486.21 | 471.6 | 731.6 | 1203.2 | 0.02013 | 0.77
| 900 | 531.98 | 526.6 | 668.8 | 1195.4 | 0.02123 | 0.5
| 1200 | 567.22 | 571.7 | 611.7 | 1183.4 | 0.02232 | 0.36
| 1500 | 596.23 | 611.6 | 556.3 | 1167.9 | 0.02346 | 0.28
| 1700 | 613.15 | 636.3 | 519.6 | 1155.9 | 0.02428 | 0.24
| 2000 | 635.82 | 671.7 | 463.4 | 1135.1 | 0.02565 | 0.19
| 2500 | 668.13 | 730.6 | 360.5 | 1091.1 | 0.0286 | 0.13
| 2700 | 679.55 | 756.2 | 312.1 | 1068.3 | 0.03027 | 0.11
| 3206.2 | 705.4 | 902.7 | 0 | 902.7 | 0.05053 | 0.05