## Instructions
Retrocommissioning Core Program Workbook Instructions
Workbook Template Valid Through 12-31-2018
Once you have completed the RCx audit and selected measures to implement, submit a Proposed Phase Workbook for pre-approval BEFORE starting implementation:
1) | Save the workbook in the format "Client - Site Address - Proposed Phase". Example; "CompanyName-1284 W State St Milwaukee 53233-Proposed.xls"
2) | Enter the information requested in the "General Information" tab.
3) | Provide a description of the project and measures on the "Project Description" tab.
4) | Create new tabs for calculations, supporting documentation, and, if necessary, supplemental summary tabs to clearly convey calculation methods and results.
• Read and follow the "Calc Guidance" and "M&V Guidance" tabs.
• If you prefer, see "M1 legacy tab" for the old RCx workbook summary tables (optional)
5) | Link the appropriate data from your new tabs to the "Measure Summary" Tab. Populate the "Estimated Savings" table and leave the "Verified Savings" table blank.
6) | Populate the Audit Cost in the "Project Costs" tab. Attach paid invoices for the audit and any supporting proposals for implementation costs.
7) | Populate the "Utility data" Tab
8) | Create a Verification monitoring plan on the "Verification Plan" tab.
9) | Provide Data from Energy Star Portfolio Manager on "Energy Star" Tab (optional)
Once you have completed implementation, submit an Implementation Phase Workbook
Use the Approved Proposed Phase Workbook, add tabs for M&V data, adjust calculations accordingly.
• Populate the "Verified Savings" table and leave the "Estimated Savings" table as is.

## General Information
Application Number
Application Name
Program Information |  | Estimated Energy Savings PROPOSED Phase
Select from drop-down |  |  |  | Peak Demand Savings (kW) | 0
Program | LEUP
Incentive Type | RCx |  | Annual | Lifecycle | Average EUL (years)
|  | kWh | 0 | 0 | 5
|  | Therms | 0 | 0 | 5
Project Information
Customer Account Name |  | PROPOSED Phase Incentives
Customer Account Tax ID |  | Audit Cost | Audit Costs | 0
|  |  | Total Estimated Costs | 0
Enrollment Date |  |  | Total Estimated Savings | #DIV/0!
Implementation Start Date |  |  | Estimated Total Incentive | 0
Implementation Completion Date |  |  | 1st Payment | 0
Implementation Probability (%) |  |  | Estimated Payback w/o Incentive | #DIV/0!
|  |  | Estimated Payback w/ Incentive | #DIV/0!
Project Information |  | Incentive as % of Project Cost |  | #DIV/0!
Customer Contact Name
Customer Contact Phone
Customer Contact email |  | Estimated Energy Savings IMPLEMENTATION Phase
|  |  |  | Peak Demand Savings (kW) | 0
Project Street Address
Project City |  |  | Annual | Lifecycle | Average EUL (years)
Project Zip Code |  | kWh | 0 | 0 | 5
|  | Therms | 0 | 0 | 5
Payment Street Address
Payment City |  | IMPLEMENTATION Phase Incentives
Payment Zip Code |  |  | Total Actual Costs | 0
Payment Attention To: |  |  | Total Verified Savings | #DIV/0!
|  |  | Final Total Incentive | 0
Service Provider Company |  |  | Remaining 2nd Payment due | 0
Service Provider Contact Name |  |  | Estimated Payback w/o Incentive | #DIV/0!
Service Provider Contact Phone |  |  | Estimated Payback w/ Incentive | #DIV/0!
Service Provider Contact Email |  | Incentive as % of Project Cost |  | #DIV/0!

## Project Description
| Application Number | 0
| Application Name | 0
Overall Site Description
-Describe facility square footage, age, and scope of study
Overall Project Description
Measure 1: |  |  | - Provide a detailed description of the overall project. - Explain exactly how energy savings resulting from the energy efficiency improvement(s) are being accomplished. - Include key details such as temperatures, pressures, dimensions, flow rates, speeds, operating hours, weights, concentrations, and other physical parameters associated with producing the energy savings. - Provide a separate description for each Measure. -Explain assumptions and calculations - Measure Numbers must be consistent with Measure Summary tab.
Measure 2:
Measure 3:
Measure 4:
Measure 5:
Measure 6:
Measure 7:
Measure 8:

## Verification Plan
| Application Number | 0
| Application Name | 0
Verification plan
Measure 1: |  |  | - Provide a detailed description of the plans to verify savings, - Describe trend data and BAS screenshots that will be provided by referencing the corresponding baseline data that has been provided within this workbook.
Measure 2:
Measure 3:
Measure 4:
Measure 5:
Measure 6:
Measure 7:
Measure 8:

## Measure Summary
Application Number | 0
Application Name | 0
Estimated Savings - Use for PROPOSED Phase Workbook
| 1st Measure | 2nd Measure | 3rd Measure | 4th Measure | 5th Measure | 6th Measure | 7th Measure | 8th Measure
Measure Name
Estimated Implementation Cost
Baseline kW
Baseline First-Year kWh
Baseline First-Year Therms
Proposed kW
Proposed First-Year kWh
Proposed First-Year Therms
kW Savings (Peak Demand) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Estimated First Year kWh Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Estimated First Year Therm Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Estimated Annual Cost Savings | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Verified Savings - Use for IMPLEMENTATION Phase Workbook
| 1st Measure | 2nd Measure | 3rd Measure | 4th Measure | 5th Measure | 6th Measure | 7th Measure | 8th Measure
Measure Name | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Actual Implementation Cost
Baseline kW
Baseline First-Year kWh
Baseline First-Year Therms
Proposed kW
Verified First-Year kWh
Verified First-Year Therms
kW Savings (Peak Demand) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Verified First Year kWh Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Verified First Year Therm Savings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Verified Annual Cost Savings | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Project Costs
Application Number |  | 0
Application Name |  | 0
Invoiced Audit Cost
Proposed Phase Estimated Implementation Costs
Measure Number | Measure Name | Implementation | Source | Explanation
1 | 0 | 0
2 | 0 | 0
3 | 0 | 0
4 | 0 | 0
5 | 0 | 0
7 | 0 | 0
7 | 0 | 0
8 | 0 | 0
Total Estimated Costs | 0
Verification Phase Actual Implementation Costs
Measure Number | Measure Name | Implementation | Source | Explanation
1 | 0 | 0
2 | 0 | 0
3 | 0 | 0
4 | 0 | 0
5 | 0 | 0
7 | 0 | 0
7 | 0 | 0
8 | 0 | 0
Total Actual Costs | 0
Attach Audit Invoices and supporting documentation for implementation Costs
Estimated costs are to be presented for each Custom Measure and an overall total cost for the project/application is to be shown.
A customer's internal costs for labor, equipment use, expendable supplies, etc. are not to be included in the estimated project costs.
The source(s) for all cost information is to be identified.
Attach supporting information such as proposals and quotations.

## Incentive Calc
Application Number | 0
Application Name | 0
Total Incentive Unit Rates
0.05 | per kWh (First Year)
0.7 | per Therm (First Year)
75% | Total Costs
1st Payment Incentive Unit Rates
0.02 | per kWh (First Year)
0.3 | per Therm (First Year)
50% | Audit Costs
PROPOSED Phase Incentive Calculation
Total Estimated First Year kWh Savings | 0
Total Estimated First Year therm Savings | 0
Total Estimated Lifecycle kWh Savings | 0
Total Estimated Lifecycle therm Savings | 0
Audit Costs | 0
Total Estimated Costs | 0
Maximum Incentive, based on savings | 0
Maximum Incentive, based on costs | 0
Maximum 1st Payment, based on savings | 0
Maximum 1st Payment, based on costs | 0
Estimated Total incentive | 0
1st Payment due | 0
Estimated 2nd Payment | 0
VERIFICATION Phase Incentive Calculation
Total Verified First Year kWh Savings | 0
Total Verified First Year therm Savings | 0
Total Verified Lifecycle kWh Savings | 0
Total Verified Lifecycle therm Savings | 0
Total Actual Costs | 0
Maximum Incentive based on savings | 0
Maximum Incentive based on costs | 0
Actual First Payment | 0
Final Total incentive | 0
Remaining 2nd Payment due | 0

## Utility Data
Application Number | 0
Application Name | 0
Utility Data Summary
Average Electric ($ per kWh) | #DIV/0! |  | Provide the following:
Average Gas ($ per Therm) | #DIV/0! |  | Electric |  | Natural Gas
Data Source Used | Customer's Actual Use Data |  | Utility Name |  | Utility Name
If Other, Specify |  |  | Account No. |  | Account No.
Customer's Utility Data
Actual use data for the latest 12 months is preferred
| Month | Year | Electric |  |  | Natural Gas
|  |  | kWh | Cost | $/kWh | Therms | Cost | $/Therm
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
[5 empty] | #DIV/0! |  |  | #DIV/0!
|  | Total | 0 | 0 |  | 0 | 0
|  | Average (Note 4) |  |  | #DIV/0! |  |  | #DIV/0!
Price Data |  |  | Notes
EIA WI Monthly Electricity Price Data
http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_6_a
Interior or 24/7 (On-Peak) | Exterior (Off-Peak)
Dollars per kWh | Dollars per kWh
EIA WI Yearly Natural Gas Price Data
http://www.eia.gov/dnav/ng/ng_sum_lsum_dcu_SWI_a.htm
Interior or 24/7 (On-Peak) | Exterior (Off-Peak)
Dollars per MCF | Dollars per Therm
Providing the data to support the average electric (kWh) and natural gas (Therm) rates listed in the Utility Data Summary above and used in the application is optional, but preferred.
If a table showing customer’s actual electric and gas use on a monthly basis for a minimum of the latest 12 months is provided (embedded with this tab), the monthly data do not need to be entered in the table above; only the annual average $/kWh and $/Therm, and annual total kWh and Therms, should be entered in the table above.
If you do not have the customer's utility history data, use the most recent U.S. Energy Information Administration (EIA) data obtained using the internet links on this tab.
Average cost is to be calculated as Total Annual kWh or Therms divided by Total Annual Costs, not by averaging the monthly $/kWh or $/Therm values.

## Energy Star
Application Number
Application Name
Insert Energy Star data here before and after the project (optional)

## Calc Guidance
Retrocommissioning Core Program Workbook Calculation Rules - Quick Reference
The following guidelines are an outline of best practices for documenting energy savings calculations for this Retrocommissioning Program.
Follow these when developing calculations for submission to focus on energy. This will ensure quicker program processing of applications,
better documentation for customers, and ensure that savings achieved by the focus on energy Retrocommissioning program meet the requirements of third party program auditors.
If you have questions about the best way to document a measure, please contact your focus on energy representative prior to investing time or resources.
https://focusonenergy.com/business/efficient-facilities/retrocommissioning
1) | Read and understand the RSP training materials provided as separate program documents before using this outline.
2) | Calculations must be submitted within an excel spreadsheet unless prior approval has been granted by implementer.
3) | Provide units clearly documented for all numbers.
4) | All cells within the spreadsheet must include a source with a clear description, e.g. measured, calculated, customer estimate if a source is not provided then the number must be linked
to other cells that are. See example below in 11).
5) | Document sources whenever possible, e.g. scanned copies of relevant spec sheet sections, photos of tool readings, screen shots, photos of nameplates, web links to referenced sources,
customer emails, etc.
6) | Measured data to determine the baseline and verified energy consumption will be expected in all possible instances show how energy use has been reduced.
7) | Measured data must sufficiently reflect operating conditions.*
8) | The same calculation method must be used to calculate before and after project energy consumption.
9) | For calculations involving BIN data use TMY3 Data that corresponds best to the project location.
10) | Assumptions upon assumptions are not allowed, e.g. square footage to calculate air flow and then air flow to calculate horsepower. For this case it is allowed to measure air flow and static
pressure to calculate horsepower.
11) | Refer to Program reviewers for acceptable assumptions that may be used when measurements are unavailable.
12) | Below is an example of how to label sources and units.
|  | Description | Value | Units | Source
Baseline Equipment Output (kWh / Part)
|  | Supply Voltage | 480 | Voltage AC | Equipment Specification Data
|  | Full Load Amperage | 200 | Amps | Avg. Trended Amps for 1 hour
|  | Power Factor | 90% | Percent | Assumed
|  | Total Full Load kW | 149.6492 | kW | Calculated
|  | Avg. Parts / Hour | 35 | Parts / Hour | Customer Observation
|  | Avg. Hours / Part | 0.028571 | Hours / Part | Calculated
|  | Avg. Element On-time / Part Forming Time | 65% | Percent | Customer Observation
|  | Time / Part Element is on | 0.018571 | Hours | Calculated
|  | Avg. kWh / Part | 2.7792 | kWh / Part | Calculated
*For guidance, see California Commissioning Collaborative, Guidelines for Verifying Savings from Commissioning Existing Buildings, Methods 2 and 3. http://www.cacx.org/

## M&VGuidance
GUIDELINES FOR UTILIZING DATA SOURCES:
All numerical data used to calculate energy savings must include a source. There are a variety of sources used while estimating energy savings. Each source of information is appropriate in certain situations and not appropriate in others. The following table shows when it is appropriate to use difference sources and how to properly document the source.
Source | When to Use | How to Use
Spot measurements of amp draw or kW | Acceptable for constant load equipment only. | - If only amp draws are available, assumptions for power factor may be made with justification. -Ideally include photos of tool readings. -Usually paired with at least 10 days of trended data regarding building operation schedules.
Trended measurements of amp draw or kW | Preferred when available. Trending required for variable operations. | -Trending should occur until sample of varied weather conditions and building schedules are large enough to represent operations. (Typically 2 weeks) -Use International Performance Measurement and Verification Protocol (IPMVP) option B or C where possible.
Trended measurements of physical data | Use to extrapolate energy measurements across a range of operation. Also, use to predict energy consumption when direct metering is unavailable. | -Use to justify all key calculation parameters. -Data points should be selected in order to allow for accurate calculations. For reference, use California Commissioning Collaborative Guidelines for Verifying Savings from Commissioning Existing Buildings, Method 2 or 3. http://www.cacx.org -Length of trend period and trending intervals should be chosen to accurately portray typical patterns for all schedules and all relevant changes in measured variables. -Trend periods for baseline and verification must have similar outdoor weather conditions.
Equipment Nameplate Data | Provide as a reference for all available related equipment. Use in calculations only if necessary. | -Nameplate Data may be utilized when measurements options are unavailable. -Relations of consumption to nameplate data must include performance curves and/or the proper conservative assumptions (see section IV). -Ideally include photos of nameplates for reference.
Source | When to Use | How to Use
Equipment Performance Curves | Use with nameplate data to estimate consumption where necessary. | -If trended amp draw or kW is not available, but pressure/temperature trending is available, then equipment performance curves may be used to calculate power draw.
Control Setpoints | Required for all pertinent equipment. | -Building automation screenshots or photos of all applicable control modules are required.
Sequence of Operations and System Schematics | Required as a reference. | -Either graphical or written documentation is acceptable. -SeqOP for the Building Automation System as well as any pertinent individual systems is typically available.
BIN DATA Calculations | Common method to extrapolate calculations across all weather conditions. | -Use consistent data sets across all calculations. -Use TMY3 Data that corresponds best to the project location.
Assumptions | Last-resort option when measurements aren’t available. | -Assumptions upon Assumptions are not allowed, e.g. assuming square footage to calculate air flow and then using assumed air flow to calculate horsepower. For this case it is allowed to measure air flow and static pressure to calculate horsepower from performance curves. -Assume ASHRAE Climatic Design Tables For Design weather conditions. -Assumptions must be more conservative, providing less energy savings than if measured data were used. -For similar equipment, reasonable statistical methods must be used to determine sample size. -Assumptions can be questioned by the program implementer or program administrator if found to not be in line with these requirements. Explanations are helpful For reviews.
Table 2: Data Source Guidelines

## M1 legacy tab
M1 legacy tab Measure Summary and Description
Application Number
Application Name
M1 legacy tab Measure Summary
Facility
Building Type
Measure Number
Measure Description :
System
Subsystem
Location
ASHRAE Climate Zone
TMY3 Weather File
M1 legacy tab Savings Summary
Electric Energy Savings | kWh/yr
Gas Energy Savings | therms/yr
Demand Savings | kW
Cost Savings | $/yr
Measure Cost | $
Simple Payback Period | years
Incentive | $
Adjusted Payback Period | years
M1 legacy tab Measured Baseline Energy Summary
Electric Energy Use | kWh/yr
Gas Energy Use | therms/yr
Electric Demand | kW
M1 legacy tab Calculated Proposed Phase Energy Summary
Electric Energy Use | kWh/yr
Gas Energy Use | therms/yr
Electric Demand | kW
M1 legacy tab Measured Verification Phase Energy Summary
Electric Energy Use | kWh/yr
Gas Energy Use | therms/yr
Electric Demand | kW
M1 legacy tab Measure Description:
1. (M1 legacy tab) Measure summary
2. (M1 legacy tab) As found conditions
3. (M1 legacy tab) Assumptions
4. (M1 legacy tab) Equations
EQ1
EQ2
EQ3
EQ4
EQ5
5. (M1 legacy tab) Methods
6. (M1 legacy tab) Instrumentation Accuracy / Specifications

## Drop-DownFuntions (hidden)
LEUP | Custom | Yes | 1.5 - year payback | Full Measure Cost | U.S. Energy Information Administration
BIP | Hybrid | No | 50% of estimated cost | Incremental Cost | State Averages
ASG |  |  | Single project cap |  | Customer's Actual Use Data
CSF |  |  | Annual customer cap |  | Other (specify)
MESP |  |  | 3 - year annual cap override agreement
Other- specify
Alex Dodd
Bill Lumsden
Don Gall
Joe Cantwell
Kevin Kohlbeck
Michael Campos
Paul Kling
Randy Urness
Richard Feustel
Steve Lewellan
Tex Reitter
Tim Hasbargen

## Measure Master Advanced Fin... (hidden)
Measure_Group | Pick_from_Measure_Group | Agriculture | Ag ID | Boilers_Burners | B&B ID | Building_Shell | BS ID | Compressed_Air_Vacuum_Pumps | CA ID | Domestic_Hot_Water | DHW ID | Food_Service | FS ID | HVAC | HVAC ID | Industrial_Ovens_and_Furnaces | IOF ID | Information_Technology | IT ID | Laundry | LDR ID | Lighting | LGT ID | Motors_Drives | M&D ID | New_Construction | NC ID | Other | O ID | Pools | PO ID | Process | PR ID | Refrigeration | RF ID | Renewable_Energy | RE ID | Waste_Water_Treatment | WWT ID | Measure Master Name | Group | Measure Master ID
Pick_from_Measure_Group | Pick Specific Measure | Grain Dryer, Energy Efficient | 2368 | Boiler Burner, Not Otherwise Specified | 2204 | Air Sealing | 2745 | Blower Purge Dryer | 223 | Domestic Hot Water, Not Otherwise Specified |  | Food Service, Not Otherwise Specified | 2320 | A/C Coil Cleaning, Ultraviolet | 2191 | Burners, Recuperative | 2233 | IT Systems, Cold Aisle Containment | 2435 | Laundry Equipment - Not Otherwise Specified | 2443 | Daylighting Controls, Automatic | 2274 | Motor, Not Otherwise Specified | 2470 | Project Savings Verification | 2970 | Benchmarking | 2746 | Pool, Not Otherwise Specified | 2493 | Furnace, Stack, Melting | 2361 | Cooler Curtain | 2268 | Project Savings Verification, Renewable Group 1 | 2976 | Aeration, Not Otherwise Specified | 2727 | Pick Specific Measure | Agriculture | Measure ID
Agriculture |  | Greenhouse Perimeter Insulation | 409 | Boiler Oxygen Trim Controls | 2207 | Building Envelope, Glazing Retrofit | 2228 | Compressed Air Heat Recovery, Non-space Heating | 2256 | Insulation, DHW Plumbing |  | Ventilation Controls, Kitchen Exhaust Hood | 2619 | Air Filtration for Exhaust Air System | 309 | Industrial Oven or Furnace, Not Otherwise Specified | 2421 | IT Systems, Not Otherwise Specified | 2436 | Laundry Heat Recovery | 232 | Delamping, Not Otherwise Specified | 2275 | [8 empty] | Process Heat Recovery, Condensing Heat Exchanger | 2497 | Cooler Economizer | 315 |  |  | Coarse Bubble Aeration | 212 | Grain Dryer, Energy Efficient | Agriculture | 2368
Boilers_Burners |  | Greenhouse Roof Vents | 2369 | Boiler System, Automatic Chemical Feed Component | 2210 | Building Envelope, Not Otherwise Specified | 2229 | Compressed Air Nozzles | 548 | Insulation, Water Heater, Not Otherwise Specified |  |  |  | Air Rotation or Air Turnover Units to Minimize Stratification | 281 | Radiant Tube Inserts, Not Otherwise Specified | 2508 | IT Systems, Server Consolidation | 2438 | Laundry, Not Otherwise Specified | 2444 | HID, Not Otherwise Specified | 2765 | [8 empty] | Process Heat Recovery, Not Otherwise Specified | 2498 | Cooler Night Covers | 2270 |  |  | Pumping, Shift To Off-peak | 2505 | Greenhouse Perimeter Insulation | Agriculture | 409
Building_Shell |  | Greenhouse Thermal blanket | 2370 | Boiler, >= 90% AFUE, NG | 2747 | Building Envelope, Reduce Air Infiltration | 2230 | Compressed Air System Isolation | 2260 | Water Heater, >90% TE, Condensing, Residential |  |  |  | Air-Conditioning Economizer, Automatic | 279 | Regenerative Thermal Oxidizer (RTO) | 2537 | IT Systems, Server Virtualization, Not Otherwise Specified | 2440 |  |  | High Intensity Discharge Lighting, Not Otherwise Specified | 2676 | [8 empty] | Process, Not Otherwise Specified | 2499 | ECM Motor, Not Otherwise Specified | 2313 |  |  | Waste Water Treatment, Not Otherwise Specified | 2650 | Greenhouse Roof Vents | Agriculture | 2369
Compressed_Air_Vacuum_Pumps |  | Irrigation Measure, Not Otherwise Specified | 2433 | Boiler, 85-90% AFUE, NG | 2748 | Building Envelope, Window Replacement | 2232 | Compressed Air, Not Otherwise Specified | 2265 | Water Heater, Fuel Switching, Electric to NG |  |  |  | Chiller Optimization Controls | 296 |  |  | IT Systems, Uninterruptible Power Supply | 2441 |  |  | Induction Lighting, Not Otherwise Specified | 2420 | [8 empty] | Pumping and Piping System Efficiency Improvement | 2504 | Evaporative Condensers Replace Air-Cooled Condensers | 2723 |  |  | Well and Pump Installation | 2664 | Greenhouse Thermal blanket | Agriculture | 2370
Domestic_Hot_Water |  | Milk Pasteurization System, Ag, Electric | 2468 | Boiler, Combustion Management System | 2213 | Insulation, Attic | 2690 | Compressed Air, Process Load Reduction | 2266 | Water Heater, Not Otherwise Specified |  |  |  | Chiller System, Not Otherwise Specified | 2247 | [6 empty] | LED, Not Otherwise Specified | 2455 | [8 empty] | Welder, Replace w/ High Efficiency Unit | 2663 | Heat Recovery, Compressor Heat Used For Space Heating | 2377 |  |  |  |  | Irrigation Measure, Not Otherwise Specified | Agriculture | 2433
Food_Service |  | Milk Pasteurization System, Ag, NG | 2469 | Boiler, Flue Gas Heat Recovery | 2215 | Insulation, Attic, Not Otherwise Specified | 2423 | Compressor, Duct in Outside Air | 2267 |  |  |  |  | Chiller System, Water Free Cooling Controls and Equipment | 2248 | [6 empty] | LED, Traffic Lights | 2459 | [10 empty] | Heat Recovery, Compressor Heat Used To Pre-heat DHW | 2378 |  |  |  |  | Milk Pasteurization System, Ag, Electric | Agriculture | 2468
HVAC |  | Plate Heat Exchanger, Milk Pipeline, VFD On Milk Vacuum Pump, Ag | 2492 | Boiler, Not Otherwise Specified | 2220 | Insulation, Ceiling | 2426 | Cycling Air Dryer | 224 |  |  |  |  | Chiller, High Efficiency, Water Cooled, Replacement | 2755 | [6 empty] | Lighting Controls, Not Otherwise Specified | 2461 | [10 empty] | Mechanical Sub-Cooling | 2464 |  |  |  |  | Milk Pasteurization System, Ag, NG | Agriculture | 2469
Industrial_Ovens_and_Furnaces |  | Thermal Curtain, Not Otherwise Specified | 2600 | Combustion Management System on Boiler | 371 | Insulation, Roof | 2428 | Variable Displacement Compressor | 525 |  |  |  |  | Demand Limiting Controls | 2278 | [6 empty] | Lighting Layout Reconfiguration | 2462 | [10 empty] | Refrigeration Economizer, Ambient Subcooling | 2511 |  |  |  |  | Plate Heat Exchanger, Milk Pipeline, VFD On Milk Vacuum Pump, Ag | Agriculture | 2492
Information_Technology |  | VFD, Not Otherwise Specified | 2645 | Insulation, Boiler Plumbing | 2425 | Insulation, Wall, Not Otherwise Specified | 2431 | [6 empty] | Desiccant Dehumidifier | 289 | [6 empty] | Lighting, Not Otherwise Specified | 2463 | [10 empty] | Refrigeration Waste Heat Recovery | 312 |  |  |  |  | Thermal Curtain, Not Otherwise Specified | Agriculture | 2600
Laundry |  | Waterer, Livestock, Not Otherwise Specified, Ag | 2661 |  |  | Overhead Door Retrofit | 2489 | [6 empty] | Destratification | 2279 | [6 empty] | T8, CEE, Not Otherwise Specified | 2589 | [10 empty] | Refrigeration, Central Parallel Rack System Replacing Individual Units | 2517 |  |  |  |  | VFD, Not Otherwise Specified | Agriculture | 2645
Lighting | [5 empty] | Overhead Door Seals | 246 | [6 empty] | Exhaust Air Heat Recovery System | 284 | [18 empty] | Refrigeration, Defrost Controls | 2518 |  |  |  |  | Waterer, Livestock, Not Otherwise Specified, Ag | Agriculture | 2661
Motors_Drives | [5 empty] | Weather Stripping Around Doors, Replacement | 2662 | [6 empty] | Fans, High Volume Low Speed (HVLS), Not Otherwise Specified | 2319 | [18 empty] | Refrigeration, Liquid Pressure Amplifiers | 2519 |  |  |  |  | Boiler Burner, Not Otherwise Specified | Boilers & Burners | 2204
New_Construction | [5 empty] | Windows, Energy Star | 2773 | [6 empty] | Heat Recovery, Not Otherwise Specified | 2379 | [18 empty] | Refrigeration, Not Otherwise Specified | 2520 |  |  |  |  | Boiler Oxygen Trim Controls | Boilers & Burners | 2207
Other | [13 empty] | HVAC Controls, Air Side Economizer, Free Cooling | 2381 | [24 empty] | Boiler System, Automatic Chemical Feed Component | Boilers & Burners | 2210
Pools | [13 empty] | HVAC Controls, Not Otherwise Specified | 2680 | [24 empty] | Boiler, >= 90% AFUE, NG | Boilers & Burners | 2747
Process | [13 empty] | HVAC Controls, Scheduling/Setpoint Optimization | 2382 | [24 empty] | Boiler, 85-90% AFUE, NG | Boilers & Burners | 2748
Refrigeration | [13 empty] | HVAC Energy Management System | 2383 | [24 empty] | Boiler, Combustion Management System | Boilers & Burners | 2213
Renewable_Energy | [13 empty] | HVAC, Low Temp System w/ Condensing Boilers | 2385 | [24 empty] | Boiler, Flue Gas Heat Recovery | Boilers & Burners | 2215
Waste_Water_Treatment | [13 empty] | HVAC, Not Otherwise Specified | 2386 | [24 empty] | Boiler, Not Otherwise Specified | Boilers & Burners | 2220
[14 empty] | HVAC, Variable Refrigerant Flow/Volume Systems | 2387 | [24 empty] | Combustion Management System on Boiler | Boilers & Burners | 371
[14 empty] | Mechanical Vent Dampers | 287 | [24 empty] | Insulation, Boiler Plumbing | Boilers & Burners | 2425
[14 empty] | Replace Constant Volume HVAC with VAV | 299 | [24 empty] | Air Sealing | Building Shell | 2745
[14 empty] | Rooftop Unit | 2539 | [24 empty] | Building Envelope, Glazing Retrofit | Building Shell | 2228
[14 empty] | Ultraviolet, Not Otherwise Specified | 2607 | [24 empty] | Building Envelope, Not Otherwise Specified | Building Shell | 2229
[14 empty] | Unit Heater, Not Otherwise Specified | 2609 | [24 empty] | Building Envelope, Reduce Air Infiltration | Building Shell | 2230
[14 empty] | Ventilation Controls | 2775 | [24 empty] | Building Envelope, Window Replacement | Building Shell | 2232
[14 empty] | Ventilation Controls, Demand Controlled Ventilation | 2722 | [24 empty] | Insulation, Attic | Building Shell | 2690
[14 empty] | Ventilation Controls, Exhaust/Supply For Paint/Spray Booth | 2724 | [24 empty] | Insulation, Attic, Not Otherwise Specified | Building Shell | 2423
[14 empty] | Ventilation Filtration vs Make Up Air System | 285 | [24 empty] | Insulation, Ceiling | Building Shell | 2426
[40 empty] | Insulation, Roof | Building Shell | 2428
[40 empty] | Insulation, Wall, Not Otherwise Specified | Building Shell | 2431
[40 empty] | Overhead Door Retrofit | Building Shell | 2489
[40 empty] | Overhead Door Seals | Building Shell | 246
[40 empty] | Weather Stripping Around Doors, Replacement | Building Shell | 2662
[40 empty] | Windows, Energy Star | Building Shell | 2773
[40 empty] | Blower Purge Dryer | Compressed Air, Vacuum Pumps | 223
[40 empty] | Compressed Air Heat Recovery, Non-space Heating | Compressed Air, Vacuum Pumps | 2256
[40 empty] | Compressed Air Nozzles | Compressed Air, Vacuum Pumps | 548
[40 empty] | Compressed Air System Isolation | Compressed Air, Vacuum Pumps | 2260
[40 empty] | Compressed Air, Not Otherwise Specified | Compressed Air, Vacuum Pumps | 2265
[40 empty] | Compressed Air, Process Load Reduction | Compressed Air, Vacuum Pumps | 2266
[40 empty] | Compressor, Duct in Outside Air | Compressed Air, Vacuum Pumps | 2267
[40 empty] | Cycling Air Dryer | Compressed Air, Vacuum Pumps | 224
[40 empty] | Variable Displacement Compressor | Compressed Air, Vacuum Pumps | 525
[40 empty] | Domestic Hot Water, Not Otherwise Specified | Domestic Hot Water | 2304
[40 empty] | Insulation, DHW Plumbing | Domestic Hot Water | 2774
[40 empty] | Insulation, Water Heater, Not Otherwise Specified | Domestic Hot Water | 2432
[40 empty] | Water Heater, >90% TE, Condensing, Residential | Domestic Hot Water | 2654
[40 empty] | Water Heater, Fuel Switching, Electric to NG | Domestic Hot Water | 2656
[40 empty] | Water Heater, Not Otherwise Specified | Domestic Hot Water | 2659
[40 empty] | Food Service, Not Otherwise Specified | Food Service | 2320
[40 empty] | Ventilation Controls, Kitchen Exhaust Hood | Food Service | 2619
[40 empty] | A/C Coil Cleaning, Ultraviolet | HVAC | 2191
[40 empty] | Air Filtration for Exhaust Air System | HVAC | 309
[40 empty] | Air Rotation or Air Turnover Units to Minimize Stratification | HVAC | 281
[40 empty] | Air-Conditioning Economizer, Automatic | HVAC | 279
[40 empty] | Chiller Optimization Controls | HVAC | 296
[40 empty] | Chiller System, Not Otherwise Specified | HVAC | 2247
[40 empty] | Chiller System, Water Free Cooling Controls and Equipment | HVAC | 2248
[40 empty] | Chiller, High Efficiency, Water Cooled, Replacement | HVAC | 2755
[40 empty] | Demand Limiting Controls | HVAC | 2278
[40 empty] | Desiccant Dehumidifier | HVAC | 289
[40 empty] | Destratification | HVAC | 2279
[40 empty] | Exhaust Air Heat Recovery System | HVAC | 284
[40 empty] | Fans, High Volume Low Speed (HVLS), Not Otherwise Specified | HVAC | 2319
[40 empty] | Heat Recovery, Not Otherwise Specified | HVAC | 2379
[40 empty] | HVAC Controls, Air Side Economizer, Free Cooling | HVAC | 2381
[40 empty] | HVAC Controls, Not Otherwise Specified | HVAC | 2680
[40 empty] | HVAC Controls, Scheduling/Setpoint Optimization | HVAC | 2382
[40 empty] | HVAC Energy Management System | HVAC | 2383
[40 empty] | HVAC, Low Temp System w/ Condensing Boilers | HVAC | 2385
[40 empty] | HVAC, Not Otherwise Specified | HVAC | 2386
[40 empty] | HVAC, Variable Refrigerant Flow/Volume Systems | HVAC | 2387
[40 empty] | Mechanical Vent Dampers | HVAC | 287
[40 empty] | Replace Constant Volume HVAC with VAV | HVAC | 299
[40 empty] | Rooftop Unit | HVAC | 2539
[40 empty] | Ultraviolet, Not Otherwise Specified | HVAC | 2607
[40 empty] | Unit Heater, Not Otherwise Specified | HVAC | 2609
[40 empty] | Ventilation Controls | HVAC | 2775
[40 empty] | Ventilation Controls, Demand Controlled Ventilation | HVAC | 2722
[40 empty] | Ventilation Controls, Exhaust/Supply For Paint/Spray Booth | HVAC | 2724
[40 empty] | Ventilation Filtration vs Make Up Air System | HVAC | 285
[40 empty] | Burners, Recuperative | Industrial Ovens and Furnaces | 2233
[40 empty] | Industrial Oven or Furnace, Not Otherwise Specified | Industrial Ovens and Furnaces | 2421
[40 empty] | Radiant Tube Inserts, Not Otherwise Specified | Industrial Ovens and Furnaces | 2508
[40 empty] | Regenerative Thermal Oxidizer (RTO) | Industrial Ovens and Furnaces | 2537
[40 empty] | IT Systems, Cold Aisle Containment | Information Technology | 2435
[40 empty] | IT Systems, Not Otherwise Specified | Information Technology | 2436
[40 empty] | IT Systems, Server Consolidation | Information Technology | 2438
[40 empty] | IT Systems, Server Virtualization, Not Otherwise Specified | Information Technology | 2440
[40 empty] | IT Systems, Uninterruptible Power Supply | Information Technology | 2441
[40 empty] | Laundry Equipment - Not Otherwise Specified | Laundry | 2443
[40 empty] | Laundry Heat Recovery | Laundry | 232
[40 empty] | Laundry, Not Otherwise Specified | Laundry | 2444
[40 empty] | Daylighting Controls, Automatic | Lighting | 2274
[40 empty] | Delamping, Not Otherwise Specified | Lighting | 2275
[40 empty] | HID, Not Otherwise Specified | Lighting | 2765
[40 empty] | High Intensity Discharge Lighting, Not Otherwise Specified | Lighting | 2676
[40 empty] | Induction Lighting, Not Otherwise Specified | Lighting | 2420
[40 empty] | LED, Not Otherwise Specified | Lighting | 2455
[40 empty] | LED, Traffic Lights | Lighting | 2459
[40 empty] | Lighting Controls, Not Otherwise Specified | Lighting | 2461
[40 empty] | Lighting Layout Reconfiguration | Lighting | 2462
[40 empty] | Lighting, Not Otherwise Specified | Lighting | 2463
[40 empty] | T8, CEE, Not Otherwise Specified | Lighting | 2589
[40 empty] | Motor, Not Otherwise Specified | Motors & Drives | 2470
[40 empty] | Project Savings Verification | New Construction | 2970
[40 empty] | Benchmarking | Other | 2746
[40 empty] | Pool, Not Otherwise Specified | Pools | 2493
[40 empty] | Furnace, Stack, Melting | Process | 2361
[40 empty] | Process Heat Recovery, Condensing Heat Exchanger | Process | 2497
[40 empty] | Process Heat Recovery, Not Otherwise Specified | Process | 2498
[40 empty] | Process, Not Otherwise Specified | Process | 2499
[40 empty] | Pumping and Piping System Efficiency Improvement | Process | 2504
[40 empty] | Welder, Replace w/ High Efficiency Unit | Process | 2663
[40 empty] | Cooler Curtain | Refrigeration | 2268
[40 empty] | Cooler Economizer | Refrigeration | 315
[40 empty] | Cooler Night Covers | Refrigeration | 2270
[40 empty] | ECM Motor, Not Otherwise Specified | Refrigeration | 2313
[40 empty] | Evaporative Condensers Replace Air-Cooled Condensers | Refrigeration | 2723
[40 empty] | Heat Recovery, Compressor Heat Used For Space Heating | Refrigeration | 2377
[40 empty] | Heat Recovery, Compressor Heat Used To Pre-heat DHW | Refrigeration | 2378
[40 empty] | Mechanical Sub-Cooling | Refrigeration | 2464
[40 empty] | Refrigeration Economizer, Ambient Subcooling | Refrigeration | 2511
[40 empty] | Refrigeration Waste Heat Recovery | Refrigeration | 312
[40 empty] | Refrigeration, Central Parallel Rack System Replacing Individual Units | Refrigeration | 2517
[40 empty] | Refrigeration, Defrost Controls | Refrigeration | 2518
[40 empty] | Refrigeration, Liquid Pressure Amplifiers | Refrigeration | 2519
[40 empty] | Refrigeration, Not Otherwise Specified | Refrigeration | 2520
[40 empty] | Project Savings Verification, Renewable Group 1 | Renewable Energy | 2976
[40 empty] | Aeration, Not Otherwise Specified | Waste Water Treatment | 2727
[40 empty] | Coarse Bubble Aeration | Waste Water Treatment | 212
[40 empty] | Pumping, Shift To Off-peak | Waste Water Treatment | 2505
[40 empty] | Waste Water Treatment, Not Otherwise Specified | Waste Water Treatment | 2650
[40 empty] | Well and Pump Installation | Waste Water Treatment | 2664